## Status
CONTRL_D DNP Status Point List
LOCATION: |  |  |  | RTU/DEVICE TYPE: |  |  |  |  | STA DC VOLTAGE: | [12 empty] | NOTE:
DATE: |  |  |  | EMS DEVICE NUM: |  |  |  |  | POINTLIST REVISION: | [12 empty] | If there is a problem with a point under test, record the issue and corrective action under the notes column here for that point along with any other needed info like eta.
DEVICE NAME: |  |  |  | RTU/SAS DNP ADDRESS: |  |  |  |  | A SYSTEM:
TDBU SAP: |  |  |  | PSC ENGINEER: |  |  |  |  | SWITCHING CENTER:
PSC SAP: |  |  |  | CRQ NUMBER: |  |  |  |  | BES ASSET: | [12 empty] | TESTING HISTORY
| CONTROL ADDRESS |  | STATUS STATE PAIR INFO |  |  | ALARMS |  |  |  |  | CROSS REFERENCE EXISTING EMS DATA |  |  |  | TAB-1 BASED | IED INFORMATION |  |  |  | INPUT | CONTROL
TAB DEC DNP INDEX | 0 BASED CONTROL ADDRESS | POINT NAME | NORMAL STATE | 1_STATE | 0_STATE | AOR | DOG_1 /3 | DOG_2 /4 | EMS TP NUMBER | VOLTAGE BASE | EXISTING DEVICE NAME | EXISTING POINT NAME | EXISTING TAB NUM | ITEM | CONTROL ADDRESS | LAN (CARD_PORT) | IED ADDRESS | I/O_REGISTER DNP_INDEX | PLC_MAPPING OBJECT_NAME | TERMINATION (BOARD_INPUT) | TERMINATION (BOARD_OUTPUT) | DATE | PSC TECH | TEST TECH | LOCAL | SYSTEM | NOTES
0 |  | DC CNTR BUS MONITOR | 1 | NORMAL | ALARM | 43 | Class 1 | Class 4 | 207019 | 0KV
1 | 0 | OXBOW 115KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207020 | 115KV
2 |  | OXBOW CUST CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207021 | 115KV
3 |  | DIXIE VALLEY CUST CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 4 | 207022 | 115KV
4 |  | 1 BANK HYDROGEN | 1 | NORMAL | ALARM | 43 | Class 1 | Class 16 | 207023 | 0KV
5 |  | 1 BANK WATER | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207024 | 0KV
6 |  | 115KV UNDERFREQ POT FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207025 | 115KV
7 | 29 | B.T. 115KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207026 | 115KV
8 | 1 | INYO E/BUS 115KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207027 | 115KV
9 | 2 | INYO W/BUS 115KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207028 | 115KV
10 | 3 | CASA DIABLO CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207029 | 115KV
11 | 4 | CASA D-SHERWIN CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207030 | 115KV
12 | 5 | HWE-INYOKERN CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207031 | 115KV
13 | 6 | COSO-HWE-IK CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207032 | 115KV
14 | 7 | BISHOP CK 3-4 CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207033 | 115KV
15 | 8 | SLP C 55KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207034 | 55KV
16 | 9 | SLP A 55KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207035 | 55KV
17 |  | INTERTIE UNDERFREQ TRIP | 1 | NORMAL | ALARM | 43 | Class 2 | Class 1 | 207036 | 0KV
18 |  | 55 UNDERFREQ CFF | 1 | NORMAL | ALARM | 43 | Class 2 | Class 1 | 207037 | 55KV
19 |  | EAST 115 BUS DIFF | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 207038 | 115KV
20 |  | WEST 115 BUS DIFF | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 207039 | 115KV
21 |  | 1 BANK SEL-387 DIFF TRIP | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 207040 | 55KV
22 |  | 1 BANK SEL-351 O/C TRIP | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 207041 | 55KV
23 | 10 | 1 BANK C-30 SUDDEN PRESSURE TRIP | 1 | NORMAL | TRIP | 43 | Class 2 | Class 4 | 207042
24 |  | 3 BANK SEL-387 DIFF TRIP | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 207043 | 55KV
25 |  | 3 BANK SEL-351 O/C TRIP | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 207044 | 55KV
26 | 11 | 3 BANK C-30 SUDDEN PRESSURE TRIP | 1 | NORMAL | TRIP | 43 | Class 2 | Class 4 | 207045
27 |  | DFR OPERATION | 1 | NORMAL | ALARM | 43 | Class 3 | Class 4 | 207046 | 0KV
28 | 12 | CASA D REACTOR | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207047 | 115KV
29 |  | CASA D REACTOR OV | 1 | NORMAL | ALARM | 43 | Class 1 | Class 16 | 207048 | 115KV
30 |  | CASA D REACTOR UV | 1 | NORMAL | ALARM | 43 | Class 1 | Class 16 | 207049 | 115KV
31 | 13 | CASA D-SHRWN REACTOR | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207050 | 115KV
32 |  | CAS D-SHRWN REAC OV | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207051 | 115KV
33 |  | CAS D-SHRWN REAC UV | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207052 | 115KV
34 |  | DFR FAILURE | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207053 | 0KV
35 |  | SPARE D35 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 207054 | 0KV
36 |  | SPARE D36 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 207055 | 0KV
37 |  | RCTR DC RLY BUS ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207056 | 115KV
38 |  | RCTR DC BCKUP BUS ALM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207057 | 115KV
39 |  | RCTR OPER BUS ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207058 | 115KV
40 |  | CASDI SHNT RCTR TRBL AL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241113 | 115KV
41 |  | CA SH SHNT RCTR TRBL AL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241114 | 115KV
42 | 25 | GATE | 1 | CLOSE | OPEN | 200 | Class 2 | Class 16 | 241115 | 0KV
43 |  | UPS TROUBLE | 1 | NORMAL | ALARM | 43 | Class 2 | Class 2 | 241116 | 0KV
44 |  | 115KV CONTRL BUS ALM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241117 | 115KV
45 |  | 115KV BACKUP BUS ALM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241118 | 115KV
46 |  | 115KV RELAY BUS | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241119 | 115KV
47 |  | 115KV OPERATING BUS | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241120 | 115KV
48 |  | 115KV ELECTRONIC BUS | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241121 | 115KV
49 |  | 115KV CB LOW AIR | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241122 | 115KV
50 |  | 55KV OPERATING BUS | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241123 | 55KV
51 |  | 55KV CONTROL BUS | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241124 | 55KV
52 |  | 55KV RELAY BUS | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241125 | 55KV
53 |  | 55KV BACKUP BUS | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241126 | 55KV
54 |  | 55KV CB MOTOR FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241127 | 55KV
55 |  | 55KV RELAY POT FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 241128 | 55KV
56 |  | 115KV CB LO GAS ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241129 | 115KV
57 | 30 | 3 BANK 115KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 241130 | 115KV
58 |  | 2 & 3 BANK HI TEMP ALM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241131 | 55KV
59 |  | 3 BANK DIFF AND O/C RLY TRBL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241132 | 55KV
60 |  | DC GROUND | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241133 | 0KV
61 |  | DC LOW VOLTAGE | 1 | NORMAL | ALARM | 43 | Class 1 | Class 4 | 241134 | 0KV
62 |  | 115KV W BUS POT ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 241135 | 115KV
63 |  | 115KV E BUS POT ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 241136 | 115KV
64 |  | SPARE D 64 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 241137 | 0KV
65 |  | 115KV SEL RELAY ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241138 | 115KV
66 |  | 55KV SEL RELAY ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241139 | 55KV
67 |  | SILVER PK PWR FLOW ALM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 4 | 241140 | 0KV
68 | 14 | 1 BANK 55KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 241141 | 55KV
69 | 15 | 3 BANK 55KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 241142 | 55KV
70 | 16 | MT. TOM 55KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 241143 | 55KV
71 | 17 | BISHOP CK 5/6 55KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 241144 | 55KV
72 | 18 | BISHOP CRK2 55KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207059 | 55KV
73 | 19 | 55KV BUSTIE CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 207060 | 55KV
74 |  | STINGER SWITCH | 1 | AUTO | SOLID | 43 | Class 3 | Class 16 | 207061 | 0KV
75 |  | SPARE D75 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 207062 | 0KV
76 |  | SPARE D76 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 207063 | 0KV
77 |  | SPARE D77 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 207064 | 0KV
78 |  | SPARE D78 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 207065 | 0KV
79 |  | SLP POWER FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 207066 | 0KV
80 | 21 | RAS N2/N1 | 1 | 2 | 1 | 43 | Class 2 | Class 4 | 241153 | 0KV
81 | 22 | RAS AUTO/OFF | 1 | AUTO | SOLID | 43 | Class 3 | Class 4 | 241154 | 0KV
82 | 23 | 3 BANK LTC AUTO/MANUAL | 1 | AUTO | MANUAL | 43 | Class 3 | Class 16 | 241155 | 55KV
83 |  | 3 BANK C-30 SUDDEN PRESSURE RELAY FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241156 | 55KV
84 | 26 | 1 BANK LTC AUTO/MANUAL | 1 | AUTO | MANUAL | 43 | Class 3 | Class 16 | 241157 | 55KV
85 |  | 1 BANK C-30 SUDDEN PRESSURE RELAY FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241158 | 55KV
86 | 28 | 1 BANK 115KV CB | 1 | CLOSE | OPEN | 43 | Class 1 | Class 3 | 241159 | 115KV
87 |  | 1 BK DIFF AND O/C RLY TRBL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241160 | 55KV
88 |  | 1 BANK GENERAL ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241161 | 55KV
89 |  | 1 BANK HI GAS ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241162 | 55KV
90 |  | 1 BANK HI TEMP ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241163 | 55KV
91 |  | 55KV CB LO GAS ALARM | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 241164 | 55KV
92 |  | SPARE D 92 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 241165 | 0KV
93 |  | TR BK SP DTT RFL 9745 RLY TRBL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 241166 | 55KV
94 |  | TR BK SP DTT RFL 9745 DTT RCVD | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 241167 | 55KV
95 |  | SPARE D 95 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 241168 | 0KV
96 |  | SEL 2030 FAIL | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227846 | 115KV
97 |  | HWE-INYOKERN A TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227847 | 115KV
98 |  | HWE-INYOKERN B TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227848 | 115KV
99 |  | HWE-INYOKERN C TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227849 | 115KV
100 |  | HWE-INYOKERN GRD TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227850 | 115KV
101 |  | COSO-HWE-IK A TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227851 | 115KV
102 |  | COSO-HWE-IK B TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227852 | 115KV
103 |  | COSO-HWE-IK C TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227853 | 115KV
104 |  | COSO-HWE-IK GRD TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227854 | 115KV
105 |  | SPARE D105 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227855 | 0KV
106 |  | SPARE D106 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227856 | 0KV
107 |  | SPARE D107 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227857 | 0KV
108 |  | SPARE D108 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227858 | 0KV
109 |  | SPARE D109 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227859 | 0KV
110 |  | SPARE D110 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227860 | 0KV
111 |  | SPARE D111 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227861 | 0KV
112 |  | SPARE D112 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 227862 | 0KV
113 |  | SILVERPEAK C A TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227863 | 55KV
114 |  | SILVERPEAK C B TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227864 | 55KV
115 |  | SILVERPEAK C C TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227865 | 55KV
116 |  | SILVERPEAK C GRD TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227866 | 55KV
117 |  | SILVERPEAK A A TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227867 | 55KV
118 |  | SILVERPEAK A B TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227868 | 55KV
119 |  | SILVERPEAK A C TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227869 | 55KV
120 |  | SILVERPEAK A GRD TGT PRI | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 227870 | 55KV
121 |  | NO.3 BANK 63X FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 227871 | 55KV
122 |  | NO.1 BANK 63X FAIL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 227872 | 55KV
123 |  | 115KV ELEC BUS AL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 227873 | 115KV
124 |  | 115KV DUPL ELEC BUS AL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 227874 | 115KV
125 |  | NO.1 GRD BK GEN AL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 227875 | 55KV
126 |  | NO.3 GRD BK GEN AL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 227876 | 55KV
127 |  | NO.2 GRD BK GEN AL | 1 | NORMAL | ALARM | 43 | Class 2 | Class 16 | 227877 | 55KV
128 |  | HWE-INYOKERN A TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9247 | 115KV
129 |  | HWE-INYOKERN B TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9248 | 115KV
130 |  | HWE-INYOKERN C TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9249 | 115KV
131 |  | HWE-INYOKERN GRD TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9250 | 115KV
132 |  | COSO-HWE-IK A TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9251 | 115KV
133 |  | COSO-HWE-IK B TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9252 | 115KV
134 |  | COSO-HWE-IK C TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9253 | 115KV
135 |  | COSO-HWE-IK GRD TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9254 | 115KV
136 |  | SILVERPEAK C A TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9255 | 55KV
137 |  | SILVERPEAK C B TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9256 | 55KV
138 |  | SILVERPEAK C C TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9257 | 55KV
139 |  | SILVERPEAK C GRD TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9258 | 55KV
140 |  | SILVERPEAK A A TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9259 | 55KV
141 |  | SILVERPEAK A B TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9260 | 55KV
142 |  | SILVERPEAK A C TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9261 | 55KV
143 |  | SILVERPEAK A GRD TGT DUP | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 9262 | 55KV
144 |  | CASA DIABLO SEL-311C RLY FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 155907 | 115KV
145 |  | CASA DIABLO SEL-311C RLY TRIP | 0 | TRIP | NORMAL | 43 | Class 2 | Class 16 | 155908 | 115KV
146 |  | CASA DIABLO SEL-311L RLY FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 155909 | 115KV
147 |  | CASA DIABLO SEL-311L CH FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 155910 | 115KV
148 |  | CASA DIABLO SEL-311L RLY TRIP | 0 | TRIP | NORMAL | 43 | Class 2 | Class 16 | 155911 | 115KV
149 |  | CASA DIABLO SEL-311L DIFF A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 16 | 155912 | 115KV
150 | 32 | CASA DIABLO SEL-311L A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 16 | 155913 | 115KV
151 |  | CASA D-SHERWIN SEL-311C RLY FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 155914 | 115KV
152 |  | CASA D-SHERWIN SEL-311C RLY TRIP | 0 | TRIP | NORMAL | 43 | Class 2 | Class 16 | 155915 | 115KV
153 |  | CASA D-SHERWIN SEL-311L RLY FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 155916 | 115KV
154 |  | CASA D-SHERWIN SEL-311L CH FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 16 | 155917 | 115KV
155 |  | CASA D-SHERWIN SEL-311L RLY TRIP | 0 | TRIP | NORMAL | 43 | Class 2 | Class 16 | 155918 | 115KV
156 |  | CASA D-SHERWIN SEL-311L DIFF A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 16 | 155919 | 115KV
157 | 33 | CASA D-SHERWIN SEL-311L A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 16 | 155920 | 115KV
158 |  | INYO L90 RLY FAIL | 0 | FAIL | NORMAL | 43 | Class 2 | Class 12 | 155921 | 24KV
159 |  | INYO L90 CH FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 6 | 155922 | 24KV
160 |  | INYO L90 RLY TRIP | 0 | TRIP | NORMAL | 43 | Class 2 | Class 12 | 155923 | 24KV
161 |  | INYO L90 DIFF A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 12 | 155924 | 24KV
162 | 34 | INYO L90 RELAY A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 12 | 155925 | 24KV
163 |  | INYO L90 DTT RECD | 0 | ALARM | NORMAL | 43 | Class 2 | Class 12 | 155926 | 24KV
164 |  | INYO SEL-311L RLY FAIL | 0 | FAIL | NORMAL | 43 | Class 2 | Class 12 | 155927 | 24KV
165 |  | INYO SEL-311L CH FAIL | 0 | ALARM | NORMAL | 43 | Class 2 | Class 6 | 155928 | 24KV
166 |  | INYO SEL-311L RLY TRIP | 0 | TRIP | NORMAL | 43 | Class 2 | Class 12 | 155929 | 24KV
167 |  | INYO SEL-311L DIFF A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 12 | 155930 | 24KV
168 | 35 | INYO SEL-311L RLY A/S | 1 | AUTO | SOLID | 43 | Class 2 | Class 12 | 155931 | 24KV
169 |  | INYO SEL-311L DTT RECD | 0 | ALARM | NORMAL | 43 | Class 2 | Class 12 | 155932 | 24KV
170 |  | SPARE D170 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155933 | 0KV
171 |  | SPARE D171 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155934 | 0KV
172 |  | SPARE D172 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155935 | 0KV
173 |  | SPARE D173 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155936 | 0KV
174 |  | SPARE D174 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155937 | 0KV
175 |  | SPARE D175 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155938 | 0KV
176 |  | SPARE D176 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155939 | 0KV
177 |  | SPARE D177 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155940 | 0KV
178 |  | SPARE D178 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155941 | 0KV
179 |  | SPARE D179 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155942 | 0KV
180 |  | SPARE D180 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155943 | 0KV
181 |  | SPARE D181 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155944 | 0KV
182 |  | SPARE D182 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155945 | 0KV
183 |  | SPARE D183 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155946 | 0KV
184 |  | SPARE D184 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155947 | 0KV
185 |  | SPARE D185 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155948 | 0KV
186 |  | SPARE D186 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155949 | 0KV
187 |  | SPARE D187 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155950 | 0KV
188 |  | SPARE D188 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155951 | 0KV
189 |  | SPARE D189 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155952 | 0KV
190 |  | SPARE D190 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155953 | 0KV
191 |  | SPARE D191 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155954 | 0KV
192 |  | SPARE D192 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155955 | 0KV
193 |  | SPARE D193 | 0 | ALARM | NORMAL | 43 | Class 16 | Class 16 | 155956 | 0KV
| 24 | NO.3 BK TAP POSITION |  | RAISE | LOWER | 43 | Class 3 | Class 16 | 203611 | 55KV
| 27 | NO.1 BK TAP POSITION |  | RAISE | LOWER | 43 | Class 3 | Class 16 | 203386 | 55KV

## Analog
CONTRL_D DNP Analog Point List
LOCATION: |  |  |  | RTU/DEVICE MODEL: |  |  |  |  | STA DC VOLTAGE: | [7 empty] | NOTE:
DATE: |  |  |  | EMS DEVICE NUM: |  |  |  |  | POINTLIST REVISION: | [7 empty] | All fullscale and limits are true values
DEVICE NAME: |  |  |  | RTU/SAS ADDRESS: |  |  |  |  | A SYSTEM:
TDBU SAP: |  |  |  | PSC ENGINEER: |  |  |  |  | SWITCHING CENTER: | [7 empty] | If there is a problem with a point under test, record the issue and corrective action under the notes column here for that point along with any other needed info like eta.
PSC SAP: |  |  |  | PSC TECHENICIAN: |  |  |  |  | TESTMAN:
EMS DATABASE INFORMATION | [12 empty] | CROSS REFERENCE INFORMATION |  |  | FIELD INFORMATION | [8 empty] | TESTING INFORMATION
|  | SCALING |  | FULL SCALE |  | LIMITS |  | ALARMS |  |  |  |  | EXISTING EMS DATA |  |  | IED INFORMATION |  |  |  |  | METERING |  |  | INPUT TERMINATION (BOARD-INPUT)
TAB DEC DNP INDEX | POINT NAME | COEFFICIENT | OFFSET | VALUE | UNIT | LOW LIMIT | HIGH LIMIT | AOR | DOG_1/3 | DOG_2/4 | EMS_TP NUMBER | VOLTAGE BASE | EXISTING DEVICE NAME | EXISTING POINT NAME | EXISTING TAB NUM | ITEM | LAN_CARD-PORT | IED_ADDRESS | I/O_REGISTER_or DNP_INDEX | PLC_MAPPING OBJECT_NAME | PT_RATIO:1V | CT RATIO:5A | SCALE_RES (OHMS) |  | DATE | PSC_TECH | TESTMAN | LOCAL | SYSTEM | NOTES
0 | ZERO REFERENCE | 0.061037 | 0 | 2000 | COUNTS | -20 | 20 | 43 | Class 16 | Class 16 | 181215 | 0KV
1 | FULL SCALE CALIBRATE | 1 | 0 | 32767 | COUNTS | 1980 | 2020 | 43 | Class 16 | Class 16 | 181216 | 0KV
2 | HWE-INYOKERN 115KV MW | 0.0027467 | 0 | 90 | MW | -76 | 76 | 43 | Class 2 | Class 2 | 181217 | 115KV
3 | COSO-HWE-IK 115KV MW | 0.0027467 | 0 | 90 | MW | -79 | 79 | 43 | Class 2 | Class 2 | 181218 | 115KV
4 | HWE-INYOKERN 115 MVAR | 0.00061037 | 0 | 20 | MVAR | -20 | 20 | 43 | Class 16 | Class 16 | 181219 | 115KV
5 | COSO-HWE-IK 115 MVAR | 0.00061037 | 0 | 20 | MVAR | -20 | 20 | 43 | Class 16 | Class 16 | 181220 | 115KV
6 | INYO 115KV MW | 0.0054933 | 0 | 180 | MW | -109 | 109 | 43 | Class 2 | Class 2 | 181221 | 115KV
7 | INYO 115KV MVAR | 0.0027467 | 0 | 90 | MVAR | -66 | 66 | 43 | Class 2 | Class 16 | 181222 | 115KV
8 | OXBOW NET MW | 0.0027467 | 0 | 90 | MW | -70 | 70 | 43 | Class 2 | Class 16 | 181223 | 115KV
9 | OXBOW NET MVAR | 0.0027467 | 0 | 90 | MVAR | -90 | 90 | 43 | Class 16 | Class 16 | 181224 | 115KV
10 | OXBOW VOLTAGE | 0.0045778 | 0 | 150 | KV | 110 | 140 | 43 | Class 2 | Class 16 | 181225 | 115KV
11 | OXBOW CURRENT | 0.0091556 | 0 | 300 | AMPS | -300 | 300 | 43 | Class 1 | Class 16 | 181226 | 115KV
12 | OXBOW GROSS MW | 0.0027467 | 0 | 90 | MW | -10 | 84 | 43 | Class 2 | Class 16 | 181227
13 | EAST BUS 115 VOLTS | 0.0045778 | 0 | 150 | KV | 116 | 124 | 43 | Class 2 | Class 4 | 181228 | 115KV
14 | WEST BUS 115 VOLTS | 0.0045778 | 0 | 150 | KV | 116 | 124 | 43 | Class 2 | Class 4 | 181229 | 115KV
15 | BISHOP CRK 3-4 MW | 0.0030519 | 0 | 100 | MW | -74 | 74 | 43 | Class 2 | Class 16 | 181230 | 115KV
16 | BISHOP CRK 3-4 MVAR | 0.0015259 | 0 | 50 | MVAR | -37 | 37 | 43 | Class 16 | Class 16 | 181231 | 115KV
17 | CASA D-SHERWIN MW | 0.0045778 | 0 | 150 | MW | -114 | 114 | 43 | Class 2 | Class 16 | 181232 | 115KV
18 | CASA D-SHERWIN MVAR | 0.0022889 | 0 | 75 | MVAR | -57 | 57 | 43 | Class 16 | Class 16 | 181233 | 115KV
19 | CASA DIABLO MW | 0.0073244 | 0 | 240 | MW | -180 | 180 | 43 | Class 2 | Class 16 | 181234 | 115KV
20 | CASA DIABLO MVAR | 0.0073244 | 0 | 240 | MVAR | -182 | 182 | 43 | Class 16 | Class 16 | 181235 | 115KV
21 | SILVER PEAK A MW | 0.0029298 | 0 | 96 | MW | -34 | 34 | 43 | Class 2 | Class 16 | 181236 | 55KV
22 | SILVER PEAK A MVAR | 0.0018311 | 0 | 60 | MVAR | -46 | 46 | 43 | Class 16 | Class 16 | 181237 | 55KV
23 | SILVER PEAK C MW | 0.0029298 | 0 | 96 | MW | -25 | 25 | 43 | Class 2 | Class 16 | 181238 | 55KV
24 | SILVER PEAK C MVAR | 0.0018311 | 0 | 60 | MVAR | -46 | 46 | 43 | Class 16 | Class 16 | 181239 | 55KV
25 | 1 BANK 115KV MW | 0.0021973 | 0 | 72 | MW | -30 | 30 | 43 | Class 2 | Class 16 | 181240 | 115KV
26 | 1 BANK 115KV MVAR | 0.0010986 | 0 | 36 | MVAR | -15 | 15 | 43 | Class 2 | Class 16 | 181241 | 115KV
27 | 3 BANK 115KV MW | 0.0021973 | 0 | 72 | MW | -40 | 40 | 43 | Class 2 | Class 16 | 181242 | 115KV
28 | 3 BANK 115KV MVAR | 0.0010986 | 0 | 36 | MVAR | -20 | 20 | 43 | Class 2 | Class 16 | 181243 | 115KV
29 | 55KV OPER BUS KV | 0.0024415 | 0 | 80 | KV | 50 | 60 | 43 | Class 2 | Class 4 | 181244 | 55KV
30 | 115KV BUS FREQUENCY | 0.00030519 | 55 | 10 | FREQ | 59 | 61 | 43 | Class 2 | Class 16 | 197282 | 115KV
31 | AMBIENT TEMPERATURE | 0.0091556 | -100 | 300 | DEG F | -10 | 150 | 43 | Class 2 | Class 16 | 197283 | 0KV
32 | 1 BANK IA | 0.018311 | 0 | 600 | AMPS | -10 | 400 | 43 | Class 2 | Class 16 | 197284 | 55KV
33 | 1 BANK IB | 0.018311 | 0 | 600 | AMPS | -10 | 400 | 43 | Class 2 | Class 16 | 197285 | 55KV
34 | 1 BANK IC | 0.018311 | 0 | 600 | AMPS | -10 | 400 | 43 | Class 2 | Class 16 | 197286 | 55KV
35 | 1 BANK IN | 0.012207 | 0 | 400 | AMPS | -10 | 380 | 43 | Class 2 | Class 16 | 197287 | 55KV
36 | 3 BANK IA | 0.018311 | 0 | 600 | AMPS | -10 | 580 | 43 | Class 2 | Class 16 | 197288 | 55KV
37 | 3 BANK IB | 0.018311 | 0 | 600 | AMPS | -10 | 580 | 43 | Class 2 | Class 16 | 197289 | 55KV
38 | 3 BANK IC | 0.018311 | 0 | 600 | AMPS | -10 | 580 | 43 | Class 2 | Class 16 | 197290 | 55KV
39 | 3 BANK IN | 0.012207 | 0 | 400 | AMPS | -20 | 380 | 43 | Class 2 | Class 16 | 197291 | 55KV
40 | NO.3 BK TAP POS | 0.9995 | 0 | 32751 | STEP | -32000 | 32000 | 43 | Class 16 | Class 16 | 197292 | 55KV
41 | INYO 115KV VOLTS | 0.0047304 | 0 | 155 | KV | 110 | 126 | 43 | Class 2 | Class 16 | 197293 | 115KV
42 | CASA D 115KV VOLT | 0.0047304 | 0 | 155 | KV | 110 | 126 | 43 | Class 2 | Class 16 | 197294 | 115KV
43 | CAS D-SHRWN 115KV VOLT | 0.0045778 | 0 | 150 | KV | 110 | 126 | 43 | Class 2 | Class 16 | 197295 | 115KV
44 | HWE-INYOKERN 115KV VOLTS | 0.0045778 | 0 | 150 | KV | 110 | 126 | 43 | Class 2 | Class 16 | 197296 | 115KV
45 | COSO-HWE-IK 115KV VOLTS | 0.0045778 | 0 | 150 | KV | 110 | 126 | 43 | Class 2 | Class 16 | 197297 | 115KV
46 | BS CK 3-4 115KV VOLTS | 0.0045778 | 0 | 150 | KV | 110 | 126 | 43 | Class 2 | Class 16 | 197298 | 115KV
47 | MT.TOM 55KV MW | 0.0010987 | 0 | 36 | MW | -28 | 28 | 43 | Class 2 | Class 16 | 197299 | 55KV
48 | MT.TOM 55KV MVAR | 0.0010987 | 0 | 36 | MVAR | -28 | 28 | 43 | Class 2 | Class 16 | 197300 | 55KV
49 | BISHOP CK 5-6 55KV MW | 0.0012207 | 0 | 40 | MW | -19 | 19 | 43 | Class 2 | Class 16 | 197301 | 55KV
50 | BISHP CK 5-6 55KV MVAR | 0.0012207 | 0 | 40 | MVAR | -19 | 19 | 43 | Class 2 | Class 16 | 197302 | 55KV
51 | BISHOP CRK2 55 MW | 0.0012207 | 0 | 40 | MW | -19 | 19 | 43 | Class 2 | Class 16 | 197303 | 55KV
52 | BISHOP CRK2 55 MVAR | 0.0012207 | 0 | 40 | MVAR | -19 | 19 | 43 | Class 2 | Class 16 | 197304 | 55KV
53 | 55KV BUSTIE MW | 0.0012818 | 0 | 42 | MW | -35 | 35 | 43 | Class 2 | Class 16 | 197305 | 55KV
54 | 55KV BUSTIE MVAR | 0.0012818 | 0 | 42 | MVAR | -35 | 35 | 43 | Class 2 | Class 16 | 197306 | 55KV
55 | SILVER PK C 55KV VOLTS | 0.0023804 | 0 | 78 | KV | 53 | 59 | 43 | Class 2 | Class 16 | 197307 | 55KV
56 | SILVER PK A 55KV VOLTS | 0.0023804 | 0 | 78 | KV | 53 | 59 | 43 | Class 2 | Class 16 | 197308 | 55KV
57 | BISHOP CRK2 55 VOLT | 0.0023804 | 0 | 78 | KV | 51 | 59 | 43 | Class 2 | Class 16 | 197309 | 55KV
58 | INYO 115KV IB | 0.04883 | 0 | 1600 | AMPS | -10 | 546 | 43 | Class 2 | Class 2 | 197310 | 115KV
59 | HWE-INYOKERN 115KV IB | 0.024415 | 0 | 800 | AMPS | -10 | 380 | 43 | Class 2 | Class 2 | 197311 | 115KV
60 | COSO-HWE-IK 115KV IB | 0.024415 | 0 | 800 | AMPS | -10 | 394 | 43 | Class 2 | Class 2 | 197312 | 115KV
61 | CASA DBLO 115KV IB | 0.018311 | 0 | 600 | AMPS | -10 | 580 | 43 | Class 2 | Class 16 | 197313 | 115KV
62 | CAS D-SHRWN 115KV IB | 0.018311 | 0 | 600 | AMPS | -10 | 580 | 43 | Class 2 | Class 16 | 197314 | 115KV
63 | BIS CK 115KV 3-4 IB | 0.012207 | 0 | 400 | AMPS | -10 | 380 | 43 | Class 2 | Class 16 | 197315 | 115KV
64 | MT.TOM 55KV IB | 0.018311 | 0 | 600 | AMPS | -10 | 580 | 43 | Class 2 | Class 16 | 197316 | 55KV
65 | SLVR PK C 55KV IB | 0.012207 | 0 | 400 | AMPS | -10 | 256 | 43 | Class 2 | Class 2 | 197317 | 55KV
66 | SLVR PK A 55KV IB | 0.012207 | 0 | 400 | AMPS | -10 | 361 | 43 | Class 2 | Class 2 | 197318 | 55KV
67 | BISHOP CRK 5-6 IB | 0.024415 | 0 | 800 | AMPS | -10 | 380 | 43 | Class 2 | Class 16 | 197319 | 55KV
68 | BISHOP CRK2 IB | 0.024415 | 0 | 800 | AMPS | -10 | 380 | 43 | Class 2 | Class 16 | 197320 | 55KV
69 | 55KV BUSTIE IB | 0.024415 | 0 | 800 | AMPS | -10 | 380 | 43 | Class 2 | Class 16 | 197321 | 55KV
70 | NO.1 BK TAP POS | 0.9995 | 0 | 32751 | STEP | -32000 | 32000 | 43 | Class 16 | Class 16 | 197322 | 55KV
71 | BUS TIE 115KV MW | 0.0018311 | 0 | 60 | MW | -54 | 54 | 43 | Class 2 | Class 16 | 197323 | 115KV
72 | BUS TIE 115KV MVAR | 0.0018311 | 0 | 60 | MVAR | -54 | 54 | 43 | Class 2 | Class 16 | 180906 | 115KV
73 | BUS TIE 115KV IB | 0.0091556 | 0 | 300 | AMPS | -3 | 270 | 43 | Class 2 | Class 16 | 180907 | 115KV
74 | SPARE A 74 | 0.061068 | 0 | 2001 | N/A | 0 | 2000 | 43 | Class 16 | Class 16 | 187822 | 0KV
75 | SPARE A 75 | 0.061068 | 0 | 2001 | N/A | 0 | 2000 | 43 | Class 16 | Class 16 | 187823 | 0KV
76 | SPARE A 76 | 0.061068 | 0 | 2001 | N/A | 0 | 2000 | 43 | Class 16 | Class 16 | 187824 | 0KV
77 | SPARE A 77 | 0.061068 | 0 | 2001 | N/A | 0 | 2000 | 43 | Class 16 | Class 16 | 187837 | 0KV
78 | SPARE A 78 | 0.061068 | 0 | 2001 | N/A | 0 | 2000 | 43 | Class 16 | Class 16 | 187838 | 0KV
79 | SPARE A 79 | 0.061068 | 0 | 2001 | N/A | 0 | 2000 | 43 | Class 16 | Class 16 | 187839 | 0KV
80 | HWE-INYOKERN FLT LOC PRI | 0.0030519 | 0 | 100 | MILES | -2 | 80 | 43 | Class 2 | Class 16 | 187840 | 115KV
81 | HWE-INYOKERN FLT LOC DUP | 0.0030519 | 0 | 100 | MILES | -2 | 80 | 43 | Class 2 | Class 16 | 187899 | 115KV
82 | CASA DIABLO FLT LOC | 0.0030519 | 0 | 100 | MILES | -2 | 80 | 43 | Class 2 | Class 16 | 187900 | 115KV
83 | CASA D-SHRWN FLT LOC | 0.0030519 | 0 | 100 | MILES | -2 | 80 | 43 | Class 2 | Class 16 | 187901 | 115KV
84 | SILVER PK C FLT LOC PRI | 0.0030519 | 0 | 100 | MILES | -2 | 80 | 43 | Class 2 | Class 16 | 187902 | 55KV
85 | SILVER PK A FLT LOC PRI | 0.0030519 | 0 | 100 | MILES | -2 | 80 | 43 | Class 2 | Class 16 | 187903 | 55KV
86 | COSO-HWE-IK FLT LOC PRI | 0.0045778 | 0 | 150 | MILES | -2 | 120 | 43 | Class 2 | Class 16 | 1734 | 115KV
87 | COSO-HWE-IK FLT LOC DUP | 0.0045778 | 0 | 150 | MILES | -2 | 120 | 43 | Class 2 | Class 16 | 1735 | 115KV
88 | SILVER PK C FLT LOC DUP | 0.0045778 | 0 | 150 | MILES | -2 | 120 | 43 | Class 2 | Class 16 | 1736 | 115KV
89 | SILVER PK A FLT LOC DUP | 0.0045778 | 0 | 150 | MILES | -2 | 120 | 43 | Class 2 | Class 16 | 1737 | 115KV